City of Berea Municipal Utilities

Electric Operations Division

200 Harrison Road

UNDERGROUND ELECTRIC SERVICE CHECKLIST

Dear Berea Municipal Utilities Resident/Contractor/Electrician,

The objective of this informational checklist is to help complete your project in a smooth and efficient manner.

ATTENTION: Only qualified City of Berea Municipal Utilities (BMU) electric personnel shall enter vaults and boxes, connect, disconnect or reconnect electric services, and/or remove/install electric meters. Non compliance with BMU requirements will result in disruption of electric service pending corrective action.

- Obtain all necessary permits

Berea City Hall Codes Enforcement, 2nd Floor 859-986-8528, online applications at www.bereaky.gov Madison County Planning & Development, 321 N. Madison Ave., Richmond,  859-624-4780

- Contact BMU Operations Secretary for the following:

  - Signing of Building Permit Application, pay all applicable fees and deposits, set up accounts.

  - All temporary and permanent new electric construction or upgrade requests, on-site coordination and inspections.

  - BEFORE YOU DIG! Call BMU Operations Department (859-986-4391, ext 2425) at least

TWO WORKING DAYS IN ADVANCE for utility service locates.

  - Schedule trench inspections with BMU Operations as follows:

    - Correct placement of service with respect to clearances and other utilities

    - Pull String required for the entire length of conduit on pulls greater than 100’.

    - Conduit – For 200 Amp, 2 ½” Schedule 40, PVC, Electrical Grade, Grey,  Min. 30” depth

For all 320-up Amp installations, 3” Schedule 40, PVC, Elect. Grade, Grey, Min. 30” depth.

- Schedule 80 PVC conduits required @ service entrance 90° bends and exposed conduit to bottom of meter base and at the power supply.

    - Conduit Bends Maximum of 2 -90° bends permitted between service entrance & power supply source unless pre-approved by BMU.

    - Rigid 90° bends may be required in trenches in excess of 150’ @ the service entrance and power supply source. This determination will be made by BMU personnel during the site visit.

    - Trenches greater than 150’ require pre-excavation site visit by BMU to determine best

route/placement of conduit.

      - On-site trench inspections are required for all trenches - before backfilling.

Before approval is given the following must be installed:

    - Ground Rods & Ground: Two  (UL listed 5/8” or 1/2” x 8’) ground rods and ground connections approved prior to backfilling (YELLOW Approval Sticker)

- Builder shall stub out 90° bend at pole with 4” spacing between pole and conduit. BMU will supply conduit running up the pole at time of connection.

- Most underground power supplies will have a 90° bend and 10’ joint of conduit in direction of lot.

BMU personnel are required to assist customer in turning 90° bend into the underground pad 	mount transformer.

- Final inspection by Codes Enforcement/Building inspector

***The above checklist must be completed before the Operations Dept. will authorize service connection. ***

Phone List:

- . BMU Operations Secretary (New construction/upgrade services) 	(859) 986 4391, ext. 2425

- . BMU Customer Service (To Pay Deposit/Billing) 			(859) 986-4391, ext. 2421

- . City Codes Enforcement/Building Department		(859) 986 8528, ext. 2127

- . Madison County Codes Enforcement/Building		                          (859) 624 4780

Please remember the customer shall insure projects conform to Berea Municipal Utilities Electric, local codes and National Electrical Code requirements.

Utilities Dept\Operations Section\BMU UG EL Service Checklist.doc